## Meters Standard Summary
Tacoma Water
Meter Standards for New Installations, Tables 1 through 3
Revised: 3/12/2018
REQUIRED:
All meters must meet applicable American Water Works Association (AWWA) standards for cold-water meters
(i.e. accuracy, performance, acceptance testing, labeling, etc.), including the following standards and any revision thereof:
C700-15, C701-15, C702-15, C703-15, C704-15, C707-10-R16, C708-15, C710-15, C712-15, C713-15, C714-13, C750-16, C751-16
Table 1. Tacoma Water Typical Meter Lay Lengths and Meter Heights, by Meter Use Type and Size
Meter Use Type | Meter Size (inches) | Meter Lay Length (inches, typical maximum) | Meter Box Type (typical) | Meter Height (typical)
Domestic/Irrigation | 5/8 | 7.5 | #3 19.75"x14.6" | 4 1/4" above center of flow line
| 5/8 X 3/4 | 7.5 | #3 19.75"x14.6" | 4 1/4" above center of flow line
| 3/4 | 9 | #3 19.75"x14.6" | 4 1/4" above center of flow line
| 1 | 10.75 | #4 22.75"x15.75" | 4 1/4" above center of flow line
| 1.5 | 13 | Armorcast 24"x36" | 4 1/4" above center of flow line
| 2 | 17 | Armorcast 24"x36" | 4 1/4" above center of flow line
| 3 | 19 | 60"x60" conc. Vault | N/A - Meter in Vault
| 4 | 23 | 60"x60" conc. Vault | N/A - Meter in Vault
| 6 | 27 | 60"x60" conc. Vault | N/A - Meter in Vault
| 8 | 30 | 60"x60" conc. Vault | N/A - Meter in Vault
| 10 | 41 | 84"x84" conc. Vault | N/A - Meter in Vault
Domestic/Fire Combo | 3/4 | 9 | #3 19.75"x14.6" | 4 1/4" above center of flow line
| 1 | 10.75 | #3 19.75"x14.6" | 4 1/4" above center of flow line
| 1.5 | 13 | Armorcast 24"x36" | 4 1/4" above center of flow line
| 2 | 17 | Armorcast 24"x36" | 4 1/4" above center of flow line
| 4 | 33 | 60"x60" conc. Vault | N/A - Meter in Vault
| 6 | 45 | 60"x60" conc. Vault | N/A - Meter in Vault
| 8 | 53 | 60"x60" conc. Vault | N/A - Meter in Vault
| 10 | 68 | 84"x84" conc. Vault | N/A - Meter in Vault
Fire Rated | 3/4 | 9 | #3 19.75"x14.6" | 4 1/4" above center of flow line
| 1 | 10.75 | #3 19.75"x14.6" | 4 1/4" above center of flow line
| 1.5 | 13 | Armorcast 24"x36" | 4 1/4" above center of flow line
| 2 | 17 | Armorcast 24"x36" | 4 1/4" above center of flow line
| 4 | 33 | 60"x60" conc. Vault | N/A - Meter in Vault
| 6 | 45 | 60"x60" conc. Vault | N/A - Meter in Vault
| 8 | 53 | 60"x60" conc. Vault | N/A - Meter in Vault
| 10 | 68 | 84"x84" conc. Vault | N/A - Meter in Vault
Large Wholesale/ Industrial/Interties /Partners | 12 | Custom Spool | 84"x84" conc. Vault or Larger | N/A - Meter in Vault
| 16 | Custom Spool | 84"x84" conc. Vault or Larger | N/A - Meter in Vault
| 20 | Custom Spool | 84"x84" conc. Vault or Larger | N/A - Meter in Vault
| 30 | Custom Spool | 84"x84" conc. Vault or Larger | N/A - Meter in Vault
Table 2. Required Meter Test Bench Flow Rates and Meter Accuracy, by Meter Sensing Type and Size
Meter Sensing Type | Meter Size (inches) | Required Meter Test Bench Flow Rates (gpm) | Required Meter Accuracy at Test Bench Flow Rates
Varies | All Sizes | Tacoma Water's meter test bench can accomodate meters up to and including 8" in size. Tacoma Water retains the option to test all meter types and sizes on a 3rd party test bench, with flow rates recommended by AWWA Standards. | AWWA Standards for Cold Water Meters (Including the following standards and any revision thereof: C700-15, C701-15, C702-15, C703-15, C704-15, C707-10-R16, C708-15, C710-15, C712-15, C713-15, C714-13, C750-16, C751-16)
Varies | Greater than 8" | Tacoma Water's meter test bench can accomodate meters up to and including 8" in size. Meters larger than 8" are tested on a 3rd party test bench, with flow rates recommended by AWWA Standards.
Table 3. Tacoma Water Typical Meter Test Bench Flow Rates and Preferred Meter Accuracy, by Meter Sensing Type and Size
Meter Sensing Type | Meter Size (inches) | Tacoma Water Typical Meter Test Bench Flow Rates (gpm) | Tacoma Water Preferred Meter Accuracy at Test Bench Flow Rates
PD (Positive Displacement) | 5/8 | 0.25 | 98.5% - 101.5%
1
10
| 5/8 X 3/4 | 0.25
1
10
| 3/4 | 0.5
2
15
| 1 | 0.75
3
25
| 1.5 | 2
5
50
90
Ultrasonic | 1.5 | 1.5
20
60
90
| 2 | 2
20
60
160
| 3 | 1
40
150
500
| 4 | 1.5
60
500
1000
| 6 | 3
120
500
1800
| 8 | 5
300
1000
1800
Omni C2 Floating Ball | 1.5 | 0.5
20
60
160
| 2 | 0.5
20
60
160
| 3 | 1
40
150
400
| 4 | 1.5
60
300
800
| 6 | 3
120
800
1600
Omni T2 Floating Ball | 1.5 | 1.5
20
60
160
| 2 | 1.5
20
60
160
| 3 | 2.5
40
150
500
| 4 | 3
60
500
1000
| 6 | 4
120
800
1800
| 8 | 5
150
800
1800
Turbine | 2 | 5
30
60
160
| 3 | 5
50
140
350
| 4 | 15
50
500
1000
| 6 | 30
500
1000
1800
| 8 | 50
500
1000
1800