| SHAFT & FLOOR PRESSURIZATION (One System per Report - Annual) | CTF 8011 | System Certification Given |
| --- | --- | --- |
| CONFIDENCE TEST | REPAIRS |  | RED |  | YELLOW |  | GREEN |
| SHAFT TYPE | STAIR | ELEVATOR | FLOOR PRESSURIZATION Yes No |
| Date of Inspection: |
| Occupancy Information |
| Occupancy Name: | Occupancy Address: |
| Building Owner: | Phone Number: | Owner Address: |
| Contact Person: | Phone Number: |
| System Information (where applicable) |
| Central Station Monitoring Yes No | Monitoring Company Name: |
| Control Panel Manufacturer: | Model Number: |
| Testing Agency Information |
| City of Tacoma Fire Protection License: | Washington State Contractor License: | NICET NUMBER: |
| Testing Agency Name: | Address: |
| Phone: | E-mail: |
| Problems Found: (Explain any “no” responses and use the back page if necessary): |
| Corrections Made: |
| Date Corrected: Corrected by: (Sign) |
| This report certifies this fire and life safety system has been properly inspected for reliability to cover the items listed in the report and is consistent with NFPA 92-A Standard. All discrepancies are noted and have been reported to the building owner or responsible person for corrective action. |
| Tech Name: (Print) | (Sign) | Date: |
| Building Representative: (Print) | (Sign) | Date: |

The items on the checklists below shall be inspected and tested. This list does not constitute all of the required inspecting and testing of the fire and life safety system. Refer to the NFPA 92-A Standard for inspecting and testing requirements.

| BUILDING SPECIFICATIONS |
| --- |
| Number of stories | Outside air temperature (F) |
| Number of stair fans | CFM | HP |
| Number of elevator fans | CFM | HP |
| Floor pressurization fans | CFM | HP |

| FAN INFORMATION |
| --- |
| Rated voltage | Actual operating voltage |
| Rated amperage | Actual operating amperage |
| Fan RPM | Number of fan belts |
| Fan belt condition | Good | Fair | Poor |

| MEASURMENTS |
| --- |
| Floor | Inches H20 | Floor | Inches H20 | Floor | Inches H20 | Floor | Inches H20 |

| PRESSURE DIFFERENCE BETWEEN FLOORS |
| --- |
| Floor | Floor | Difference in H20 | Floor | Floor | Difference in H20 | Floor | Floor | Difference in H20 |

| INSPECTION INFROMATION | YES | NO |
| --- | --- | --- |
| 1. Were measurements taken from atmospheric pressure? |  |  |
| 2. Were measurements taken from shaft and the main occupied area? |  |  |
| 3. What was static pressure? | In. H20 |  |  |
| 4. Were readings taken at every 5th floor? |  |  |
| 5. Do fans operate when fire alarm is activated? |  |  |
| 6. If no sprinklers, is the elevator shaft pressure 0.15 in H20 or greater? |  |  |
| 7. Do elevator shaft pressures measure 0.10 in H20, in 100% automatic sprinklered building? |  |  |
| 8. All doors (stairway and elevator operate correctly?) |  |  |
| 9. Can system be operated manually? |  |  |
| 10. Does life safety core type building have 0.05 in H20 between pressurized core and tenant area? |  |  |
| 11. Are gaskets in good condition on stair and elevator doors? |  |  |
| 12. Do all dampers, controls work properly on shaft pressurization system? |  |  |
| 13. Do stair shaft pressures measure 0.15 in H20? |  |  |

Problems Found:

Corrections Made:

# Text boxes

# Tacoma Fire Department
Confidence Test Officer 253.591.5740
3471 S. 35th St. Tacoma, WA 98409

# tfdcto@cityoftacoma.org